Work Completion Report

To,

The Executive Engineer

Betul Dv. Betul D.C.

Madhya Pradesh Madya/Paschim/Poorv Vidyut Vitran Company Sir/Madam.

Sub:	Submission of work completion report (to be submitted by the applicant) for system documentation requirements.

Ref:	Our Application Registration No.: NP-MPMK26-14534479

With reference to the above, I hereby confirm to you that we have completed the work of installation of the renewable energy system and submit the following basic information for your perusal and request you to arrange to inspect and commission the system at the earliest:

# Details of the Solar PV module

  - Model No. BiN-08-535

  - Name and address of manufacturer: Waaree Energies Limited

  - Capacity of each Module (Wp) : 535

  - No. of Modules: 9

  - Total Capacity (kWp): 4.82

  - Date of installation: 15-09-2026

# Details of the Inverter

  - Name and address of the inverter manufacturer: Polycab

  - Brand Name of the inverter: Polycab

  - Model No. PSIS-5K0

  - AC capacity of individual inverter (kW): 5kw

  - No. of inverters installed :1

  - Total AC capacity of inverter (kW) :5kw

  - Serial Nos. 5K0110826-2626-404353P

  - Date of installation 15-09-2026

# Details of the Cables: DC

  - Make / Name of manufacturer: Polycab-DC

  - Size & Type: 4 Sqmm , single core , copper

# Details of the AC wiring

  - Make/Name of manufacturer : Polycab -AC

  - Size & Type : 4 Sqmm , single core , copper

# Details of the DC distribution box

  - Make/Name of manufacturer : Havells

  - Sl. No. NA

  - DC Surge Protection Device: single SPD

  - MCB/Isolator quantity & capacity : ISOLATORS-1

  - Size & Type : 05 KW moisture proof

# Details of the AC distribution box

  - Make/Name of manufacturer : Havells

  - Sl. No. N.A.

  - AC Surge Protection Device : Device : single SPD

  - MCB/MCCB quantity & capacity: ISOLATORS-1

  - Size & Type: 05 KW moisture proof

# Details of Battery Bank (if applicable)

  - Make / Name of manufacturer

  - Type of battery

  - Sr. Nos.

  - Capacity of each Cell (V / AH)

| 1. | Number of Cells in series |  |
| --- | --- | --- |
| 2. | Number of Cells in parallel |  |
| 3. | Total capacity in AH |  |
| 4. | Total battery bank voltage |  |

# Details of the Earthing

| 1. | Earth resistance (Shall be less than 2 ohms) | 1.2 ohms |
| --- | --- | --- |
| 2. | Size of the Earth wire / flat* | 4 Sqmm Cu |
| 3. | Two separate Earthing points Modules & DC Surge arrester Inverter, AC Surge protection device & Lightening Arrester | Yes |
| 4. | Size & Type | Copper and G.I. |

# Details of the Net meter details (please enclose the test report of the bi-directional meter tested at the laboratory of the Discom)

| 1. | Make |  |
| --- | --- | --- |
| 2. | Serial No. |  |
| 3. | Capacity |  |
| 4. | Type / Model |  |
| 5. | Single ph. / Three ph. |  |
| 6. | CT Ratio |  |
| 7. | Date of Test by MT, Discom |  |

- Details of the Caution signage

- Provision of manual and automatic switches: Yes

- G.P.S. Co-ordinates of the Renewable Energy System Installation

(i) Latitude: 21.8840185	(ii) Longitude: 77.9016424

# Whether Operation and Maintenance Manual provided to the consumer: Yes

Certified that the above said renewable energy system was installed and the equipment used complies with the Technical and Safety standards as specified by the Discom under net metering program.

Name and Signature of the System Installer

Name of the firm and address

Bhim Energy Solutions

Near Delhivery office,

Athner Road , Badora,

BETUL

Signature of the Applicant

Name and Address with Seal

Krishni Nagde

SHARDA NAGAR GAUTHANA RANIPUR ROAD GAUTHANA BETUL

# Enclosures:

- Test report of net meter tested at the laboratory of the Discom.

- Copy of the IEC/IS Test certificates of PV modules, Inverter etc.

- Data sheets/Drawing for the array mounting System.

- Actual Single line wiring diagram (SLD) of the SPV System.

- Copy of Maintenance & Operation information manual provided by the System Installer. Copy of Interconnection Agreement on non-judicial stamp paper of Rs. 500/- with Discom.